## Header
Site Name:
Site Code:
Address:
City | Washington
State | DC
Zip Code
Donor Site | One Judiciary Sq.
Prepared by:
On:
Company:
Tel:
Email
UL calculator | v3.0 2019-05-29

## OUC Assumptions
Assumptions
In Building Noise Floor / sensitivity |  | -118 | dBm
Max power from OUC unit
mobile radio |  | 45.4407 | dBm
portable |  | 36 | dBm
OUC safety factor added manufacturer's specs
Level above which BDA may be damaged |  | 10 | dB
Level above which BDA will clip |  | 6 | dB
OUC factor for per channel max power on a composite power
OUC downlink active channels | 20 | 13.01 | dB
OUC uplink simultaneous channels used directly under a single DAS antenna | 2 | 3.01 | dB
OUC uplink simultaneous channels (on DAS) | 6 | 7.78 | dB
OUC sites |  | Noise floors |  | Latitude | Longitude | EiRP (dBm) | Uplink Gain | Azimuth (°) | DL Antenna | UL Antenna
4D |  | -117 | dBm | 38.963 | -77.0267 | 48.6923 | 17 | 225 | Sinclair SE419SF3P4LDF | Sinclair SC412HF2LDF
Fletcher Johnson |  | -114 | dBm | 38.8842 | -76.9333 | 53.2015 | 18 | 200 | Sinclair SE419SF3P4LDF | Sinclair SC412HF2LDF
George Washington Univ. Hosp |  | -114 | dBm | 38.9016 | -77.0485 | 48.9209 | 16 | 0 | Sinclair SC412HF2LDF | Sinclair SC412HF2LDF
Georgetown Univ. Hosp. |  | -115 | dBm | 38.9114 | -77.0759 | 54.8996 | 12 | 0 | Sinclair SC412HF2LDF | Sinclair SC412HF2LDF
One Judiciary Sq. |  | -112 | dBm | 38.8954 | -77.0156 | 54.0993 | 18 | 0 | Sinclair SC412HF2LDF | Sinclair SC412HF2LDF
Reeves Ctr. |  | -117 | dBm | 38.9172 | -77.0324 | 54.0993 | 16 | 0 | Sinclair SC412HF2LDF | Sinclair SC412HF2LDF
Rhode Island |  | -115 | dBm | 38.9275 | -76.9803 | 53.7475 | 17 | 0 | Sinclair SC412HF2LDF | Sinclair SC412HF2LDF
Sibley Hospital |  | -116 | dBm | 38.9368 | -77.1083 | 53.3041 | 16 | 110 | Sinclair SE419SF3P4LDF | Sinclair SC412HF2LDF
St. Elizabeth's Hospital |  | -110 | dBm | 38.8489 | -76.9864 | 53.2015 | 19 | 310 | Sinclair SE419SF3P4LDF | Sinclair SC412HF2LDF
UDC Bldg. 41 |  | -115 | dBm | 38.9439 | -77.0664 | 51.9866 | 16 | 125 | Sinclair SE419SF3P4LDF | Sinclair SC412HF2LDF

## Designer's Settings
Designer Inputs
RF Conditions Estimates
Targeted OUC donor site transmitted power (EiRP) | 54.0993 | dBm
MAX Estimated downlink RSSI from Host site at BDA input [Host Site EiRP] - [FreeSpace Path Loss] + [donor antenna gain] + [Targeted Site Uplink Gain] = * See "OUC Assumptions" tab | -23 | dBm
BDA and DAS Equipment manufacturer's specifications
Max BDA uplink input power | [5 empty] | Designer Inputs
Level above which the BDA may sustain damage | 10 | dBm | BDA Configuration
Level above BDA normal operations level (Clip, shutdown or wideband AGC) vendor specific. If not published use [Max UL Tx Power] - [Gain] + [per ch dynamic gain/Level control] | -8 | dBm | Configured BDA uplink gain | 95 | dB
MAX (Composite uplink) Transmitted Power Output the BDA is capable of (clip level) | 27 | dBm | BDA uplink max AGC | 60 | dB
DAS Configuration |  |  | BDA max Squelch (attenuation not threshold) | 60 | dB
DAS Antenna gain | 2 | dBi | Additional Recommended Attenuation
Minimum cable and combiner loss from BDA to DAS antennas | 14 | dB | External padding required at UL input to prevent BDA damage (passive only) | 0 | dB
Closest distance a subscriber can approach a DAS antenna |  |  | Additional padding required at UL input to ensure BDA operational power (passive or wideband digital) | 15.0207 | dB
Mobile | 10 | ft. | Total input attenuation needed | 15.0207 | dB
Portable | 6 | ft. | Additional attenuation to protect ouc site (output) | 0 | dB
Expected Performance
|  |  | Max allowed noise tranmission level | -49.9007 | dBm
|  |  | Expected uplink noise level transmitted by BDA as configured | -38.0207 | dBm
|  |  | Expected uplink noise level as configured/w sqlch | -98.0207 | dBm
Donor Antenna
DAS System Contributed Noise
=
Rcc
+
NDAS
–
Gtr
+
Delta
Measuring DAS Noise Contribution
Booster
Field
Strength
Field
Strength
In
-
Building
f
1
Host TX
Rcc
=
Measured receive control channel
(
dBm
)
NDAS
=
Measured noise at output of booster
(
dBm
)
Gtr
=
Transmit power of GTR
8000
(
50
dBm
)
Delta
=
Difference in Tx
/
Rx budget for site
(
dB
)
Client Antenna

## Objectives vs. Measurements
OUC Performance Requirements
C/I objective at host receiver | 18 | dB
Max accepted power at OUC host sites' receivers | -45 | dBm
Target for received noise at host site is | 15 | dB | below the noise floor
Donor - Host RF Conditions Measured
Host site receiver noise floor (measured) | -115 | dBm
Uplink signal transmitted through donor antenna and measured at host site receiver | -40 | dBm
Transmitted power through the donor antenna for path loss measurement(account for any duplexors or coax that is bypassed in measurement) | 35 | dBm
Propagation Loss Donor Antenna -> Host receive | 75 | dB
Digital input attenuation configured | -23 | dB
These values will be affected by gain setting and should be evaluated after that is set
Design Objectives vs. Measurements |  |  | Objective vs. Measured
Max Permitted Transmitted Power Output from BDA per channel | 30 | dBm
Max noise transmit power from BDA: applies to quiescent amplifer as well as non keyed channels when single channel is keyed | -55 | dBm | output padding may be necessary to meet output power or noise requirements | -51
Max BDA input uplink power (BDA input) | -21.78 | dBm | Max signal received from Mobile at Active UL input (After attenuation) | -18 | dBm
|  |  | Max signal received from Portable at Active UL input (After attenuation) | -18 | dBm

## Design Computations
OUC BDA Gain Worksheet
Numbers in red must be supplied by integrator (see "Designer Settings" tab)
Numbers in green are calculated values
OUC supplied
TPO = Transmitter Power Output
Max uplink signal to OUC
Max accepted power at OUC sites | -45 |  | dBm | ='Objectives vs. Measurements'!B3
Host site receiver noise floor (estimated) | -112 |  | dBm | =VLOOKUP(Header!B9,'OUC Assumptions'!B19:D28,3,FALSE)
Target for received signal at host site | 15 |  | dB | ='Objectives vs. Measurements'!B4
OUC max noise contribution | -127 |  | dBm | =B11-B12
OUC site power(EiRP) | 54.0993 |  | dBm | ='Designer''s Settings'!B3
Uplink RSSI from donor site at BDA input (account for: free space loss, donor antenna gain, uplink gain specified for the targetedd site in the "OUC Assumptions" tab | -23 |  | dBm | ='Designer''s Settings'!B4
BDA uplink path loss (calculated) | 77.0993 |  | dB | =B14-B15
Max Permitted TPO from BDA per channel | 32.0993 |  | dBm | =B10+B16
Max noise transmit power from BDA applies to quiescent amplifer as well as non keyed channels when single channel is keyed | -49.9007 |  | dBm | =B13+B16
BDA Equipment limits
Max input power of BDA (vendor) | 10 | -8 | dBm | ='Designer''s Settings'!B7 | ='Designer''s Settings'!B8
OUC uplink simultaneous channels rating (single DAS antenna/DAS) | 3.01 | 7.78 |  | ='OUC Assumptions'!D13 | ='OUC Assumptions'!D14
OUC safety factor to manufacturer's specs | 10 | 6 | dB | ='OUC Assumptions'!D9 | ='OUC Assumptions'!D10
Max BDA input power (per channel) | -3.01 | -21.78 | dBm | =B21-B22-B23 | =C21-C22-C23
BDA input limits | mobile radio | portable
Max power from OUC Portable/mobile unit | 45.4407 | 36 | dBm | ='OUC Assumptions'!D6 | ='OUC Assumptions'!D7
Minimum cable and combiner loss from BDA to DAS antennas | 14 | 14 | dB | ='Designer''s Settings'!B12 | =B28
Closest distance a subscriber can approach a DAS antenna | 10 | 6 | ft. | ='Designer''s Settings'!B14 | ='Designer''s Settings'!B15
Calculated Free Space Loss between the subscriber and the DAS antenna | 40.2 | 35.8 | dB | =ROUNDUP(20*LOG10(B29/3.28084)+20*LOG10(800)-27.55,1) | =ROUNDUP(20*LOG10(C29/3.28084)+20*LOG10(800)-27.55,1)
DAS Antenna gain | 2 | 2 | dBm | ='Designer''s Settings'!B11 | =B31
Pathloss from subscriber to BDA uplink input (calculated) | 52.2 | 47.8 | dB | =B28-B31+B30 | =C28-C31+C30
Max calculated BDA input uplink power (before attenuation) | -6.7593 | -11.8 | dBm | =B27-B32 | =C27-C32
External padding req at UL input to prevent BDA damage | 0 | 0 | dB | =MAX(B33-$B24,0) | =MAX(C33-$B24,0)
Additional padding (above damage padding) required at UL input to ensure BDA operational (may be digital padding) | 15.0207 | 9.98 | dB | =MAX(B33-$C24-B34,0) | =MAX(C33-$C24-C34,0)
BDA uplink output limits
MAX composit TPO BDA is capable of (clip level) | 27 |  | dBm | ='Designer''s Settings'!B9
Single DAS antenna multi channel rating | 3.01 |  | dB | ='OUC Assumptions'!D13
OUC safety factor | 6 |  | dB | ='OUC Assumptions'!D10
Max uplink derated for multi channel and ouc safety | 17.99 |  | dBm | =B38-B39-B40
Max power BDA can produce as configured (ignoring AGC) | 73.22 |  | dBm | =MAX(B33,C33)-B52-B53+B43
Configured BDA uplink gain | 95 |  | dB | ='Designer''s Settings'!F8
BDA uplink max AGC | 60 |  | dB | ='Designer''s Settings'!F9
Max uplink transmitted power permitted to input and transmit | 17.99 |  | dBm | =MIN(B17,B41)
Max power BDA should produce as configured | 27 |  | dBm | =(MIN(B38,B42))
Max BDA input to stay below amplifier clip limit | -17.01 |  | dBm | =B41-B43+B44
Gain reduction needed to stay below OUC host site receiver limit | 0 |  | dB | =MAX((B46-B17),0)
Max input for protection and output clip | -21.78 |  | dBm | =MIN(B24:C24,B47)
BDA settings
Passive attenuation needed at uplink input | 0 |  | dB | =MAX(B34:C34)
Passive or digital attenuation needed | 15.0207 |  | dB | =MAX(B35:C35)
Expected noise Level as configured | -38.0207 |  | dBm | ='OUC Assumptions'!D4+'Designer''s Settings'!F8-'Designer''s Settings'!F14-'Designer''s Settings'!F15
Expected noise Level as configured/w sqlch | -98.0207 |  | dBm | ='OUC Assumptions'!D4+'Designer''s Settings'!F8-'Designer''s Settings'!F14-'Designer''s Settings'!F15-'Designer''s Settings'!F10

## Testing Computations
OUC BDA Gain Worksheet | [5 empty] | Pass/Fail
Numbers in red must be supplied by integrator (see "Designer Settings" tab)
Numbers in green are calculated values
OUC supplied
TPO = Transmitter Power Output
Max uplink signal to OUC
Max accepted power at OUC sites | -45 |  | dBm | ='Objectives vs. Measurements'!B3
Host site receiver noise floor (measured) | -115 |  | dBm | ='Objectives vs. Measurements'!B7
Target for received signal at host site | 15 |  | dB | ='Objectives vs. Measurements'!B4
OUC max noise contribution | -130 |  | dBm | =B11-B12
OUC site power(EiRP) |  |  | dBm
Uplink RSSI from donor site at BDA input (account for: free space loss, donor antenna gain, uplink gain specified for the targetedd site in the "OUC Assumptions" tab |  |  | dBm
BDA Path Loss (measured) | 75 |  | dB | ='Objectives vs. Measurements'!B9-'Objectives vs. Measurements'!B8
Max Permitted TPO from BDA per channel | 30 |  | dBm | =B10+B16
Max noise transmit power from BDA applies to quiescent amplifer as well as non keyed channels when single channel is keyed | -55 |  | dBm | =B13+B16
BDA Equipment limits
Max input power of BDA (vendor) | 10 | -8 | dBm | ='Designer''s Settings'!B7 | ='Designer''s Settings'!B8
OUC uplink simultaneous channels rating (single DAS antenna/DAS) | 3.01 | 7.78 |  | ='OUC Assumptions'!D13 | ='OUC Assumptions'!D14
OUC safety factor to manufacturer's specs | 10 | 6 | dB | ='OUC Assumptions'!D9 | ='OUC Assumptions'!D10
Max BDA input power (per channel) | -3.01 | -21.78 | dBm | =B21-B22-B23 | =C21-C22-C23
BDA input limits | mobile radio | portable
Max power from OUC Portable/mobile unit | 45.4407 | 36 | dBm | ='OUC Assumptions'!D6 | ='OUC Assumptions'!D7
Minimum cable and combiner loss from BDA to DAS antennas | 14 | 14 | dB | ='Designer''s Settings'!B12 | =B28
Closest distance a subscriber can approach a DAS antenna | 10 | 6 | ft. | ='Designer''s Settings'!B14 | ='Designer''s Settings'!B15
Calculated Free Space Loss between the subscriber and the DAS antenna | 40.2 | 35.8 | dB | =ROUNDUP(20*LOG10(B29/3.28084)+20*LOG10(800)-27.55,1) | =ROUNDUP(20*LOG10(C29/3.28084)+20*LOG10(800)-27.55,1)
DAS Antenna gain | 2 | 2 | dBm | ='Designer''s Settings'!B11 | =B31
pathloss from subscriber to BDA uplink input (measured) |  |  | dB
Max calculated BDA input uplink power (before attenuation) | -18 | -18 | dBm | ='Objectives vs. Measurements'!E20 | ='Objectives vs. Measurements'!E21
External padding req at UL input to prevent BDA damage |  |  | dB
Additional padding (above damage padding) required at UL input to ensure BDA operational (may be digital padding) |  |  | dB
BDA uplink output limits
MAX composit TPO BDA is capable of (clip level) | 27 |  | dBm | ='Designer''s Settings'!B9
Single DAS antenna multi channel rating | 3.01 |  | dB | ='OUC Assumptions'!D13
OUC safety factor | 10 |  | dB | ='OUC Assumptions'!D9
Max uplink derated for multi channel and ouc safety | 13.99 |  | dBm | =B38-B39-B40
Max power BDA can produce as configured (ignoring AGC) | 100 |  | dBm | =MAX(B33,C33)-B53+B43
Configured BDA uplink gain | 95 |  | dB | ='Designer''s Settings'!F8
BDA uplink max AGC | 60 |  | dB | ='Designer''s Settings'!F9
Max uplink transmitted power permitted to input and transmit | 13.99 |  | dBm | =MIN(B17,B41)
Max power BDA should produce as configured | 27 |  | dBm | =(MIN(B38,B42))
Max BDA input to stay below amplifier clip limit | -21.01 |  | dBm | =B41-B43+B44
Gain reduction needed to stay below OUC host site receiver limit | 0 |  | dB | =MAX((B46-B17),0)
Max input for protection and output clip | -21.78 |  | dBm | =MIN(B24:C24,B47)
BDA settings
Passive attenuation needed at uplink input
Passive or digital attenuation needed | -23 |  | dB | ='Objectives vs. Measurements'!B12
Expected noise Level as configured | 60 |  | dBm | ='OUC Assumptions'!D5+'Designer''s Settings'!F9-'Designer''s Settings'!F15-'Designer''s Settings'!F16
Expected noise Level as configured/w sqlch | 60 |  | dBm | ='OUC Assumptions'!D5+'Designer''s Settings'!F9-'Designer''s Settings'!F15-'Designer''s Settings'!F16-'Designer''s Settings'!F11