## Header P25
Test Date: | 2018-02-20 | Result |  | 4D | PASS
Site Code & Name: | PR-72 Wharf 1 |  |  | George Washington Univ. Hosp | FAIL
Fletcher Johnson
Building Manager contact info: |  | Building rep.technical contact info: |  | Georgetown Univ. Hosp.
Tel: |  | Company: |  | One Judiciary Sq.
Company: |  | Tel: |  | Reeves Ctr.
Address: |  | Email: |  | Rhode Island
City, State Zipcode |  |  |  | St. Elizabeth's Hospital
Email: |  | OUC rep. technical Name |  | UDC Bldg. 41
Company:
Emergency Contact info |  | Tel:
Company: |  | Email:
Tel:
Email: |  | Fiber DAS HeadEnd located in room
|  | Number of remotes | 1
BDA located in room: |  | Fiber DAS Brand/Model Number
BDA Brand/Model Number |  | FiberDAS HeadEnd UL Received signal
IP address |  | FiberDAS HeadEnd DL Received signal
UserName
Password |  | Donor Site Name | 0
|  | Host Site Noise Reference Level | 0
BDA Uplink Gain | 0 | Path Loss (dB) | 0
BDA Downlink Gain | 0 | BDA UL Output noise | 0
BDA Uplink Squelch Threshold |  | Noise Contribution to host site | 0
Isolation |  | Max signal received at donor site | 0
|  | Min signal received at donor site | 0
Description of building readiness & other comments as necessary

## Check List P25
Date |  | 2018-02-20 | R | 0
Site |  | PR-72 Wharf 1
TESTING | Reference in ATP requirements doc | Required | PASS | FAIL | Value | Comment (include what failed/passed)
Head End Room
Grounding | Section 4.4
NEMA4-Type Enclosure BDA | Section 4.4
NEMA4-Type Enclosure Fiber DAS Headend | Section 4.4
NEMA4-Type Enclosure Batteries | Section 4.4
Labeling (cables, antennas, Remotes) | Section 4.4
Enclosure signage | Section 4.4
Rooftop
Antenna | Section 4.4
Grounding | Section 4.4
Surge Arrestor | Section 4.4
Top 3 UL Sites
Top 3 UL RSSI
Donor Site | Section 4.4
Bda pathloss
Path Loss(unpadded) | Section 4.7-A
Control Channel DL RSSI
BDA/Headend Battery/Alarming
Battery Verification | Section 4.4
Battery Back up Test | Section 4.4
Local shut down test
Alarms | Section 4.4
Remote access to BDA | Section 4.3
BDA Check
29 Frequencies programmed (UL & DL) | Section 4.5
Channels 12.5 kHz wide | Section 4.5
Spectrum scan check | Section 4.5 |  |  |  |  | Attach screen capture
Level check across band | Section 4.5
Uplink gain adjustment
Host noise measurement | Section 4.6-1
Near Signal measurement @ BDA Input
BDA Coverage pad UL/DL
Active DAS coverage pads entered on DAS Tab
Near Signalmeasurement @ host after adjustment | Section 4.6-3
Lowest signal measurement @ host after adjustment | Section 4.6-3
UL Gain | Section 4.6-3
DL Gain | Section 4.6-3
Near-Far Test | Section 4.6-4
Noise measurement out of BDA | Section 4.7-B
Donor Hard Pad
Uplink Noise contribution evaluation | Section 4.7-B |  |  |  | 0
Squelch adjustment
Uplink DAS noise measurement | Section 4.8
Squelch Threshold | Section 4.8
Isolation Test | Section 4.9
Update of link Budget UL completed
Update link Budget DL completed
Frequencies availability verification (BDA or Remotes Tab | Section 4.10
Commercial DAS interference check (if applicable) | Section 4.11
Private LMR radio system interference check (if applicable) | Section 4.11
Audio Test results (DAQ 3.4) | Section 4.12
Coverage Test plot and statistics (-95 dBm) | Section 4.13
Remote access to monitoring | Section 4.3
DAS Antennas RSSI measurements baseline (Remotes check tab) | Section 4.13
Note on F4: GuyJouannelle: Fill in highlighted cells

## Remotes Check P25
|  | Date: |  |  |  |  | 2018-02-20
|  | Site: |  |  |  |  | PR-72 Wharf 1
|  | Number of Remotes: | [8 empty] | 1
[7 empty] | Frequencies | [29 empty] | OK
|  | Remotes | Room Location | Labeling | Battery battery Check | Battery function Check | Channel 1 | Channel 2 | Channel 3 | Channel 4 | Channel 5 | Channel 6 | Channel 7 | Channel 8 | Channel 9 | Channel 10 | Channel 11 | Channel 12 | Channel 13 | Channel 14 | Channel 15 | Channel 16 | Channel 17 | Channel 18 | Channel 19 | Channel 20 | Channel 21 | Channel 22 | Channel 23 | Channel 24 | Channel 25 | Channel 26 | Channel 27 | Channel 28 | Channel 29 | Hot Link Level | KO | Attenuation Added | Hotlink after attenuation
1 | 1 | Remote 01 | Room 1 | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 0
8 | 0
9 | 0
10 | 0
11 | 0
12 | 0
13 | 0
14 | 0
15 | 0
16 | 0
17 | 0
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
25 | 0
26 | 0
27 | 0

## Coverage Baseline P25
Date: | 2018-02-20
Site: | PR-72 Wharf 1
|  | Fringe areas: | Those are elevators lobbies, exist stairs, exit path ways, emergency and standby power rooms, and any location the testing sowed the coverage was the weakest.
|  | Area ID | Name | RSSI | Location description
|  | 1 | Rm 510 |  | residential room minimal coverage
|  | 2 | Garage 1 |  | mechanical rooms.
ANTENNA BASELINE REFERENCE LEVELS
fail
|  | Floor 13 |  |  | Floor 12 |  |  | Floor 11 |  |  | Floor 10
|  | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI
[5 empty] | BDA | ant 41 | -52 |  |  |  | Remote 1 | ant 38 | -52
[5 empty] | BDA | ant 42 | -58 |  |  |  | Remote 2 | ant 39 | -58
[5 empty] | BDA | ant 43 | -58 |  |  |  | Remote 1 | ant 40 | -58
|  | Floor 9 |  |  | Floor 8 |  |  | Floor 7 |  |  | Floor 6
|  | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI
[5 empty] | Remote 1 | ant 1 | -55 | BDA | ant 33 | -58 | BDA | ant 4 | -48
[5 empty] | Remote 1 | ant 2 | -58 |  |  |  | BDA | ant 5 | -52
[5 empty] | Remote 1 | ant 3 | -62 |  |  |  | BDA | ant 3 | -52
[11 empty] | BDA | ant 34 | -65
|  | Floor 5 |  |  | Floor 4 |  |  | Floor 3 |  |  | Floor 2
|  | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI
[5 empty] | BDA | ant 7 | -50 | BDA | ant 10 | -45 | BDA | ant 13 | -45
[5 empty] | BDA | ant 8 | -50 | BDA | ant 11 | -50 | BDA | ant 14 | -45
[5 empty] | BDA | ant 9 | -50 | BDA | ant 12 | -48 | BDA | ant 15 | -35
[5 empty] | BDA | ant 35 | -55 | BDA | ant 36 | -55 | BDA | ant 16 | -40
[11 empty] | BDA | ant 37 | -58
|  | Floor 1 |  |  | Floor B1 |  |  | Floor B2
|  | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI | Active. # | Ant. Label | RSSI
|  | BDA | ant 17 | -50 | BDA | ant 22 | -60 | BDA | ant 28 | -55
|  | BDA | ant 18 | -58 | BDA | ant 23 | -60 | BDA | ant 29 | -60
|  | BDA | ant 19 | -60 | BDA | ant 21 | -60 | BDA | ant 27 | -58
|  | BDA | ant 20 | -58 | BDA | ant 24 | -52 | BDA | ant 30 | -55
[5 empty] | BDA | ant 25 | -65 | BDA | ant 31 | -65
[5 empty] | BDA | ant 26 | -55 | BDA | ant 32 | -65